## Calculator HVDC
HVDC
Power | 800 | MW
voltage level | 600 | kV
Number cables | 1 | nr
Conductor diameter | 50 | mm
Cable lenght | 1000 | km
Current | 1333.3333 | A
Conductor area | 0.0019625 | m2
Resistivity | 8.5605e-06 | ohm/m
Power loss factor | 15.2187 | kW/km
Power loss over distance | 15.2187 | MW
Power transfer losses | 1.902%
[6 empty] | 2% |  | 1.902% | 2%
Power loss total system | 5.902% |  | Copper | 1.68e-08 | [Ohm m]
Today, two HVDC cable technologies are installed:
Single core mass impregnated or self-contained fluid filled (SCFF) cables:
This type of cable is currently the most used. It has been in service for more than 40 years, has proven highly reliable and can be provided by European manufacturers at voltages up to +/- 500 kV and 1400 A DC which corresponds to a maximum pole rating of 660 MW (in service) and bipole rating of 1320 MW. Conductor sizes are typically up to 2500 mm2.
Cross linked polyethylene (XLPE) cables:
XLPE cables are only used in Voltage Source Converters applications that allow to reverse the power flow without reversing the polarity.
To date this technology is in service at voltages up to +/- 320 kV and 800 MW up to 1000 MW, with voltages up to +/- 600 kV now qualified for use.
Convertor loss
Convertor loss
Cable loss